## bus
| name | vn_kv | type | zone | in_service
0 | Terrasa | 110 | b |  | TRUE
1 | Manresa | 110 | b |  | TRUE
2 | Tarrega | 110 | b |  | TRUE
3 | Montblanc | 110 | b |  | TRUE
4 | Vandellos | 110 | b |  | TRUE
5 | Lleida | 110 | b |  | TRUE
6 | Igualada | 110 | b |  | TRUE
7 | El Perellos | 110 | b |  | TRUE
8 | Agramunt | 110 | b |  | TRUE
9 | Valls | 110 | b |  | TRUE
10 | Manresa_LV | 20 | b |  | TRUE
11 | Tarrega_LV | 20 | b |  | TRUE
12 | Montblanc_LV | 20 | b |  | TRUE
13 | Lleida_LV | 20 | b |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | Load_manresa | 10 | 70 | 0 | 0 | 0 |  | 1 | TRUE | wye
1 | Load_tarrega | 11 | 100 | 0 | 0 | 0 |  | 1 | TRUE | wye
2 | Load_montblanc | 12 | 70 | 0 | 0 | 0 |  | 1 | TRUE | wye
3 | Load_lleida | 13 | 70 | 0 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type
0 |  | 4 | 200 | 1 |  |  |  | 1 | FALSE | TRUE | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | Line0 | single | 0 | 1 | 23 | 0.062 | 0.404 | 8.935 | 0 | 0.9 | 1 | 1 |  | TRUE
1 | Line1 | double | 1 | 2 | 58 | 0.031 | 0.188 | 19.26 | 0 | 1.8 | 1 | 1 |  | TRUE
2 | Line2 | double | 2 | 3 | 30 | 0.031 | 0.188 | 19.26 | 0 | 1.8 | 1 | 1 |  | TRUE
3 | Line3 | double | 3 | 4 | 52 | 0.031 | 0.188 | 19.26 | 0 | 1.8 | 1 | 1 |  | TRUE
4 | Line4 | single | 2 | 5 | 44 | 0.062 | 0.404 | 8.935 | 0 | 0.9 | 1 | 1 |  | TRUE
5 | Line5 | single | 2 | 6 | 40 | 0.062 | 0.404 | 8.935 | 0 | 0.9 | 1 | 1 |  | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 |  | 100MVA | 1 | 10 | 100 | 110 | 20 | 18 | 0.38 | 22 | 0.04 | 150 | hv | 0 | -9 | 9 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE
1 |  | 200MVA | 2 | 11 | 200 | 110 | 20 | 12.2 | 0.26 | 65 | 0.06 | 0 | hv | 0 | -9 | 9 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE
2 |  | 100MVA | 3 | 12 | 100 | 110 | 20 | 18 | 0.38 | 22 | 0.04 | 150 | hv | 0 | -9 | 9 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE
3 |  | 100MVA | 5 | 13 | 100 | 110 | 20 | 18 | 0.38 | 22 | 0.04 | 150 | hv | 0 | -9 | 9 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2.0179 | 41.5668
1 | 1.8169 | 41.724
2 | 1.1395 | 41.6469
3 | 1.1618 | 41.3748
4 | 0.87562 | 40.9562
5 | 0.61613 | 41.6154
6 | 1.6191 | 41.5807
7 | 0.71262 | 40.8754
8 | 1.0866 | 41.7915
9 | 1.2476 | 41.2843
10 | 1.8121 | 41.7152
11 | 1.1518 | 41.6416
12 | 1.154 | 41.3747
13 | 0.61427 | 41.6126

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
single | 8.935 | 0.062 | 0.404 | 0.9
double | 19.26 | 0.031 | 0.188 | 1.8

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
100MVA | 0.04 | 22 | 0.38 | 100 | 20 | 110 | 18 | 150 | YNdS | hv | 0 | -9 | 9 | 0 | 2.5 | FALSE
200MVA | 0.06 | 65 | 0.26 | 200 | 20 | 110 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | float64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | ext_grid | name | object
28 | ext_grid | bus | uint32
29 | ext_grid | vm_pu | float64
30 | ext_grid | va_degree | float64
31 | ext_grid | slack_weight | float64
32 | ext_grid | in_service | bool
33 | line | name | object
34 | line | std_type | object
35 | line | from_bus | uint32
36 | line | to_bus | uint32
37 | line | length_km | float64
38 | line | r_ohm_per_km | float64
39 | line | x_ohm_per_km | float64
40 | line | c_nf_per_km | float64
41 | line | g_us_per_km | float64
42 | line | max_i_ka | float64
43 | line | df | float64
44 | line | parallel | uint32
45 | line | type | object
46 | line | in_service | bool
47 | trafo | name | object
48 | trafo | std_type | object
49 | trafo | hv_bus | uint32
50 | trafo | lv_bus | uint32
51 | trafo | sn_mva | float64
52 | trafo | vn_hv_kv | float64
53 | trafo | vn_lv_kv | float64
54 | trafo | vk_percent | float64
55 | trafo | vkr_percent | float64
56 | trafo | pfe_kw | float64
57 | trafo | i0_percent | float64
58 | trafo | shift_degree | float64
59 | trafo | tap_side | object
60 | trafo | tap_neutral | int32
61 | trafo | tap_min | int32
62 | trafo | tap_max | int32
63 | trafo | tap_step_percent | float64
64 | trafo | tap_step_degree | float64
65 | trafo | tap_pos | int32
66 | trafo | tap_phase_shifter | bool
67 | trafo | parallel | uint32
68 | trafo | df | float64
69 | trafo | in_service | bool
70 | bus_geodata | x | float64
71 | bus_geodata | y | float64
72 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.13.1 | 2.12.0 | FALSE | FALSE |  | 50 | 1